## BoQ1 (hidden)
Percentage BoQ
BoQ_Ver3.1 | Percentage | Normal | INR Only | INR
Select, At Par, Excess (+), Less (-) |  | IOCL
Tender Inviting Authority: Superinteding Engineer, Institute Works Department, IIT(BHU), Varanasi
Name of Work: Supply, Installing, Testing and Commissioning of ‘Silent Type 125 KVA Diesel Generator in the Dhanrajgiri Hostel-2 IIT(BHU) Varanasi
Contract No: IIT(BHU)/IWD/
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 7 | 54 | 8
0.1 | xx | BI01010001010000000000000515BI0100001112 | [52 empty] | 0.1 | xx | BI01010001010000000000000515BI0100001112 |  |  | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1 | Supply, Installing, Testing and Commissioning of ‘Silent Type 125 KVA Diesel Generating set 415 volts at 1500 RPM, 0.8 lagging power factor at 415 V suitable for 50Hz, 3 phase system at NTP conditions and consisting of the followings: A. Diesel Engine: Diesel engine 4 stroke, Six cylender, water cooled, electric start, of suitable BHP at 1500 RPM suitable for above output of alternator at NTP conditions and conforming to BS 5514/ISO3046, BS 649, IS 10000, capable of taking 10% over loading for one hour after 12 hour of continuous operation. The engine will be fitted complete with all the required accessories with ATS/AMF.Make-Cumins Jakson/Caterpillar/Lyland/Kirloskar/TATA B. Engine mounted Instrument Panel fitted with and having digital display for following: (i) Start-stop switch with key (ii) Water temperature indication (iii) Lubrication oil pressure indication (iv) Lubrication oil temperature indication (v) Battery charging indication (vi) RPM indication (vii) Over speed indication (viii) Low lub. Oil trip indication (ix) Engine Hours indication C. Alternator: Synchronous alternator Stamford make rated at 125 KVA, 415 volts at 1500 RPM, 3 phase 50 Hz, AC supply with 0.8 lagging power factor at NTP conditions. The alternator shall be having SPDP enclosure, brushless, continuous duty, self-excited and self-regulated through AVR conforming to IS: 4722/BS 2613 suitable for tropical conditions and with class-F/H insulation.+/-1.5%Voltage Regulation (max),IP23 Protection with class-H Insulation,Permanent lumbricating bearing,permissible overload of 10% for one hour in 12 hours of opertaion.Make-Stanford/Leroy-Somer/Mecc Alte D. Base Frame Both the engine and alternator shall be mounted on suitable base frame made of MS channel with necessary reinforcement which shall be installed on existing cement concrete foundation and i/c supplying & fixing of suitable vibration isolation arrangement as per recommendations of manufacturer. E. Exhaust System: Dry exhaust manifold with Residential exhaust silencer and catalytic convertor i/c all supporting structure,Turbocharger,Companion flanges for silencer & bellow F. Starting System 12V/24V DC starting system comprising of starter motors voltage regulator and arrangement for initial excitation complete with suitable nos of batteries (25 plate 100 AH lead acid type) as reqd as per specifications. G. Acoustic and weather proof enclosure with arrangement for fresh air intake for cooling of the engine & alternator, extraction, discharging hot air in to the atmosphere as per specifications. H. AMF Panel Fabricating, insatalling testing and commisioning of automatic mains failure control panel (PS-500) cincluding auto by-pass panel, suitable for 125 KVA silent type DG Set complete with relays, timers, set of CTs of metering & protection and energy analyser to frequency power factor, KWH, KVARH & provision for overload, short circuit, restricted earth fault, under frequency, control cabling from AMF panel to diesel engine and elsewhere if require all complete and inter locking including the following: i. 1 No.200Amps 4 P MCCB 36 KA (Ics =100% Icu) Make-L&T/SEIL/ABB/C&S ii. 2 Nos.200 amp Contactar iii. Auto/ Manual/ Test/ Off Selector switch iv. 2 Nos. over voltage relay , 2 Nos. reverse power relay and 2 Nos. under voltage relay. v. 1 Set of 3 Nos. current transformers. vi Energy analyser unit to indicate current voltage frequency power factor and KWH vii. Indicating lamps for load on mains and load on set viii. Suitable MCB for instruments ix. Battery charger, complete with transformer / rectifier DC voltemeter and ammeter selector switch for trickle off and boost and current adjustment x. Main supply failure monitor xi. Supply failure timer xii. Restoration timer xiii. Control unit with three impulse automatic engine start / stop and failure to start lockout. xiv. impulse counter with locking and reset facility xv. ON/ OFF / Control circuit switch with indicater xvi. Audio/ Video annunciation for a. Low lubricating oil pressure b. Engine over speed c. Engine fails to start d. Full load/ maximum load warning e. High water tempreture Fuel Tank Daily service Fuel tank not less than 270 liter liters fabricated from 14SWG sheet metal built inside base frame complete with drain valve,air vent,inlet & outlet connection | BI01010001010000000000000515BI0100001113 | 1 | No | 1256700 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1256700 | 1256700 | INR Twelve Lakh Fifty Six Thousand Seven Hundred Only | 1 | Trenching in ordinary soil up to a depth of 60 cm including removal andstacking of serviceable materials and then disposing of surplus soil, byspreading and neatly levelling within a lead of 50 m and making up thetrenched area to proper levels by filling with earth or earth mixed withsludge or / and manure before and after flooding trench with water (excludingcost of imported earth, sludge or manure). (2.1) | BI01010001010000000000000515BI0100001113 | 1446 | Cum | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
Total in Figures | [51 empty] | 1256700 | 1256700 | INR Twelve Lakh Fifty Six Thousand Seven Hundred Only |  |  |  |  | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | INR Zero Only
Quoted Rate in Words |  | INR Zero Only
Note on K13: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K14: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.

## Macros
Please Enable Macros to View BoQ information