## BoQ1 (hidden)
Percentage BoQ
BoQ_Ver3.1 | Percentage | Normal | INR Only | INR
Select, At Par, Excess (+), Less (-) |  | IOCL
Tender Inviting Authority: Superinteding Engineer, Institute Works Department, IIT(BHU), Varanasi
Name of Work: BOQ for Supply,Installation,Testing ,Fixing,and Mounting of LED Flood Light on existing High Mast Lighting Pole in the Gymkhana Ground IIT(BHU)
Contract No: IIT(BHU)/IWD/ET-09/2022-23/883 Dated 08.09.2022
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 7 | 54 | 8
0.1 | xx | BI01010001010000000000000515BI0100001112 | [52 empty] | 0.1 | xx | BI01010001010000000000000515BI0100001112 |  |  | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1 | Supply,Installation,Testing ,Fixing,and Mounting of LED Flood Light fixture on existing High Mast Lighting Pole height-21 to 25 Meter in the Gymkhana Ground including all accessries & wiring works. Minimum wattage rating-900W to1000W suitable for stadium lighting,Lighting lumen output not less than 112500 lumens,System Efficacy not less than -125 lm/Watt with beam angle, the luminaire shall have a CRI>70,CCT 5700K to 6000K,IP/IK- 66/08 .The luminaire is made of Die casting Aluminium ADC1 housing,Powder painting RAL9007 and anti dust exposed lense, Surge Protection internal 4 KV & external 10 to15 KV.Input voltage range 140-170 V, P.F>0.95,THD<10%,Wind force IEC/GB Standared, area<0.4 sqm.Salt spray test 1000hrs.Safety & service class-1.Replaceable Driver Burning Hour 50Khrs L70B50@Ta35C outdoor,CB/CE,RoHS Compliance, Life class -50000 hrs, Lumen efficacy @ L70,Toughened Glass quality- IK07, Protection Class-IP66, Luminaire & Driver should be BIS certified, in house NABL.i/c connection with 1.5 sqmm FRLS PVC insulated Copper conductor single core cable and earthing etc. Make-Philipse/ Wipro/Crompton/ Bajaj/Havells/Ventura | BI01010001010000000000000515BI0100001113 | 60 | Nos | 90625 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | #VALUE! | #VALUE! | #VALUE! | 1 | Supply,Installation,Testing ,Fixing,and Mounting of LED Flood Light fixture on existing High Mast Lighting Pole height-21 to 25 Meter in the Gymkhana Ground including all accessries & wiring works. Minimum wattage rating-900W to1000W suitable for stadium lighting,Lighting lumen output not less than 112500 lumens,System Efficacy not less than -125 lm/Watt with beam angle, the luminaire shall have a CRI>70,CCT 5700K to 6000K,IP/IK- 66/08 .The luminaire is made of Die casting Aluminium ADC1 housing,Powder painting RAL9007 and anti dust exposed lense, Surge Protection internal 4 KV & external 10 to15 KV.Input voltage range 140-170 V, P.F>0.95,THD<10%,Wind force IEC/GB Standared, area<0.4 sqm.Salt spray test 1000hrs.Safety & service class-1.Replaceable Driver Burning Hour 50Khrs L70B50@Ta35C outdoor,CB/CE,RoHS Compliance, Life class -50000 hrs, Lumen efficacy @ L70,Toughened Glass quality- IK07, Protection Class-IP66, Luminaire & Driver should be BIS certified, in house NABL.i/c connection with 1.5 sqmm FRLS PVC insulated Copper conductor single core cable and earthing etc. Make-Philipse/ Wipro/Crompton/ Bajaj/Havells/Ventura | BI01010001010000000000000515BI0100001113 | 60 | Nos | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
Total in Figures | [51 empty] | #VALUE! | #VALUE! | #VALUE! |  |  |  |  | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | #VALUE!
Quoted Rate in Words |  | #VALUE!
Note on K13: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K14: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Validate
Print
Help

## Macros
Please Enable Macros to View BoQ information