## BoQ1 (hidden)
Percentage BoQ
BoQ_Ver3.1 | Percentage | Normal | INR Only | INR
Select, At Par, Excess (+), Less (-) |  | IOCL
Tender Inviting Authority: Superinteding Engineer, Institute Works Department, IIT(BHU), Varanasi
Name of Work: Supply, Installing, Testing and Commissioning of ‘Silent Type 82.5 KVA Diesel Generator in the Faculty apartment IIT(BHU)
Contract No: IIT(BHU)/IWD/ET-11/2022-23/871 Dated 07.09.2022
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 7 | 54 | 8
0.1 | xx | BI01010001010000000000000515BI0100001112 | [52 empty] | 0.1 | xx | BI01010001010000000000000515BI0100001112 |  |  | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1 | Supply, Installation, Testing and Commissioning of 82.5 KVA / 66 KW silent diesel generating set comprising of Prime Duty Engine with 10% overload capacity in 12 hours operation, developing 104.56 BHP at 1500 RPM, 04 Cylinder, Electronic Governor A0, dry type filters, radiator, 170 Ltrs fuel tank, 12V Electric Start, Residential Silencer inside the Acoustic Enclosure, Coolant Cooled with Radiator, 82.5KVA, 50Hz, 1500 RPM, 415V single bearing, synchronous alternator, self starter, 12V 90AH battery with leads. The lube oil change period or service interval should be 600 hours or 1 year whichever occur first. Make-Cumins Jakson/Caterpillar/Lyland/Kirloskar/TATA Genset Protections: Low lube oil pressure and High coolant temperature Alternator: alternator, efficiency not below than 92.4% at 100% load, self-excited self-regulated developing 82.5 KVA output, 415Volt, 50 Hz, 1500 RPM, screen protected drip proof confirming IS:4722/13364 standard.Make-Leroy-Somer/Crompton/Stamford Mounting: The Engine and Alternator are directly coupled and mounted on common base frame with suitable AVM pads.including foundation. Fuel Tank: Fuel tank with 170 liters capacity, complete with fuel piping etc. AMF Control Panel: The AMF control panel approved by CPRI in the name of DG Set manufacturer for IP:54, HV & IR Tests according to IS/IEC : 61439 comprising of 2Nos 4P, 200A, Power Contactors for DG Supply & Mains Supply complete with 2 Nos 200A 4P MCCB’s, Mains supply bypass changeover of 200A, REF Relay with standard CT’s, Reverse Power Relay, Aluminium Busbar and other standard accessories as per OEM. Acoustic Enclosure: Acoustic enclosure preteated by 11 tank process made out CRCA Sheet with PP based powder coating as per ARAI guildelines and follow CPCB-II norms. Lifting hooks provide for unloading purpose. Residential silencer should be mounted inside the canopy. | BI01010001010000000000000515BI0100001113 | 1 | No. | 1067900 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1067900 | 1067900 | INR Ten Lakh Sixty Seven Thousand Nine Hundred Only | 1 | Trenching in ordinary soil up to a depth of 60 cm including removal andstacking of serviceable materials and then disposing of surplus soil, byspreading and neatly levelling within a lead of 50 m and making up thetrenched area to proper levels by filling with earth or earth mixed withsludge or / and manure before and after flooding trench with water (excludingcost of imported earth, sludge or manure). (2.1) | BI01010001010000000000000515BI0100001113 | 1446 | Cum | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
Total in Figures | [51 empty] | 1067900 | 1067900 | INR Ten Lakh Sixty Seven Thousand Nine Hundred Only |  |  |  |  | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | INR Zero Only
Quoted Rate in Words |  | INR Zero Only
Note on K13: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K14: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.

## Macros
Please Enable Macros to View BoQ information