## BoQ1 (hidden)
Percentage BoQ
BoQ_Ver3.1 | Percentage | Normal | INR Only | INR
Select, At Par, Excess (+), Less (-) |  | IOCL
Tender Inviting Authority: Superinteding Engineer, Institute Works Department, IIT(BHU), Varanasi
Name of Work: Supply,Installation,Testing and Commisiononing of Cubical outdoor LT Panel and Earthing Works in the Metallurgical Engineering Department IIT(BHU)
Contract No: IIT(BHU)/IWD/ Dated
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT With Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 7 | 54 | 8
0.1 | xx | BI01010001010000000000000515BI0100001112 | [52 empty] | 0.1 | xx | BI01010001010000000000000515BI0100001112 |  |  | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1 | Supply,Installation,Testing & Commisionioning (SITC) of Out door CPRI certified cubical Feeder pilal with EC grade Al busbar capacity 630 Amp 100% neutral suitable >25kA for 3 sec for fault level, compatiable for following incomming & outgoing. Custum built self fabricated out of 16 SWG ,CRCA sheet Foot mounted type Panel Furnished with siemen gray shade powder coated paint after necessary pre treatment fully dust & vermin proof . Copper Wire , Lugs and Hardware EC Grade Al Busbar 630A Three Phase and Neutral & InsulatingMaterial Engineering and Labor Charges. Panel Size :( H-,W-,D-)mm.Incomer detail -SFU-630 Amp,TPN 2 Nos & 6Nos-HRC fuse, Incomer Al Busbar capacity 630 Amp.Outgoing Details-TP MCCB-400 Amp,4 Nos . Make-L&T /ABB /GE /SCHNEIDER /SIEMENS with sufficient capacity outgoing Al busbar. | BI01010001010000000000000515BI0100001113 | 1 | Lot | 485000 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 485000 | 485000 | INR Four Lakh Eighty Five Thousand Only | 1 | Trenching in ordinary soil up to a depth of 60 cm including removal andstacking of serviceable materials and then disposing of surplus soil, byspreading and neatly levelling within a lead of 50 m and making up thetrenched area to proper levels by filling with earth or earth mixed withsludge or / and manure before and after flooding trench with water (excludingcost of imported earth, sludge or manure). (2.1) | BI01010001010000000000000515BI0100001113 | 1446 | Cum | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
2 | Earthing with G.I. earth pipe 4.5 metre long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc | BI01010001010000000000000515BI0100001114 | 1 | nos. | 5308 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 5308 | 5308 | INR Five Thousand Three Hundred & Eight Only | 2 | Supplying and stacking of good earth at site including royalty and carriage upto 5 km lead complete (earth measured in stacks will be reduced by 20% for payment). (2.2) | BI01010001010000000000000515BI0100001114 | 482 | Cum | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
3 | Supplying and laying 25 mm X 5 mm G.I strip at 0.50 metre below ground as strip earth electrode, including connection/ terminating with G.I. nut, bolt, spring, washer etc. as required. (Jointing shall be done by overlapping and with 2 sets of G.I. nut bolt & spring washer spaced at 50mm) | BI01010001010000000000000515BI0100001115 | 10 | Mtr | 131 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1310 | 1310 | INR One Thousand Three Hundred & Ten Only | 3 | Supplying and stacking sludge at site including royalty and carriage upto 5km lead complete (sludge measured in stacks will be reduced by 8% for payment). (2.3) | BI01010001010000000000000515BI0100001115 | 241 | Cum | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
4 | Supply , Construction ,Plaster & Masionary work of 2 No Pedestal fondaion size-3X1X5 Feet for mounting of Feeder Pilar. | BI01010001010000000000000515BI0100001116 | 1 | Job | 8000 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 8000 | 8000 | INR Eight Thousand Only | 4 | Supplying and stacking at site dump manure from approved source, including carriage upto 5 km lead complete (manure measured in stacks will be reduced by 8% for payment) : Screened through sieve of I.S. designation 16 mm (2.4.2) | BI01010001010000000000000515BI0100001116 | 241 | Cum | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
Total in Figures | [51 empty] | 499618 | 499618 | INR Four Lakh Ninety Nine Thousand Six Hundred & Eighteen Only |  |  |  |  | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | INR Zero Only
Quoted Rate in Words |  | INR Zero Only
Note on K13: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K14: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K15: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K16: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.
Note on K17: gepadmin: 1. If you choose "Full Conversion" then Column BA (AMOUNT) and Column BB (TAXES) BOTH values will be convert based on selected Currency in (Column L). 2. If you choose "Partial Conversion" then Column BA (AMOUNT) only will be converted based on selected currency (Column L) and Column BB (TAXES) value (INR) will be added to the converted values.

## Macros
Please Enable Macros to View BoQ information